QuickSize

Generator Set Sizing

Project		Mini Project

Customer	VTC

___________________________________________________________

Generator Set

Model No.	900ROZD4	Gensets	1

Engine	16V2000 G61 (Diesel)

Alternator	5M4044

___________________________________________________________

Performance Summary

LN / LL Voltage	219/380	volts	Altitude		50	meters

Frequency	50	hertz	Ambient Temp.	25	C

Phase(s)	3	phase

Genset Rating @ 130C Rise	808.00 kW

Genset Derated Rating	808.00 kW

Total Running Power	390.00 kW

Percent of Available kW Used	48.27 %

Alternator Starting kVA	2650.00 kVA @ 35% dip

Peak Starting kVA	913.70 kVA

Percent of Available kVA Used	34.48 %

Maximum Voltage Dip	13.64 %

Maximum Frequency Dip	3.94 %	( no restriction )

Voltage THD	0.00 %	( no restriction )

___________________________________________________________

Informational

Program Version	8.0.0

Database Version	1.6

Project Created	December 22, 2020; 07:22:14 PM

Project Last Saved	December 22, 2020; 07:22:14 PM

Report Created	December 22, 2020; 08:09:46 PM

Project Created By

QuickSize

Generator Load Profile

Project		Mini Project

Customer	VTC

___________________________________________________________

Generator Set

Model No.	900ROZD4	Gensets	1

Engine	16V2000 G61 (Diesel)

Alternator	5M4044

___________________________________________________________

Load Profile

Run	Run	Run	Start	Start	Volt	Freq	Volt (L-N)

Qty	kW	kVA	pF	kW	kVA	Dip	Dip	THD

Step #1	Load Step #1

Light  (Incandesent lighting)

1	0.00	0.00	?.??	0.00	0.00

Emergency Light and power  (Floresent lighting with low distortion electronic ballast)

1	100.00	100.00	1.00	100.00	100.00

Fireman Lift  (20.000 kW, 3 phase, code F, loaded motors, w/ 300% solid start starting)

Rated motor torque from full voltage starting = 24.9%

2	40.00	46.91	0.85	60.51	140.72

Fixed Fire Pump  (20.000 kW, 3 phase, code F, loaded, fire pump motor, w/ wye-delta starting)

Rated motor torque from full voltage starting = 24.8%

1	20.00	23.45	0.85	38.07	88.53

Sprinkler Pump  (40.000 kW, 3 phase, code F, loaded, fire pump motor, w/ wye-delta starting)

Rated motor torque from full voltage starting = 24.8%

1	40.00	48.20	0.83	66.92	180.86

Jockey Pump  (5.000 kW, 3 phase, code H, loaded, fire pump motor, w/ A.T.L. starting)

Rated motor torque from full voltage starting = 74.6%

1	5.00	5.75	0.87	20.93	35.47

Passenger Lift  (20.000 kW, 3 phase, code F, loaded motors, w/ 300% solid start starting)

Rated motor torque from full voltage starting = 24.9%

6	120.00	140.73	0.85	181.53	422.16

____________________________________________________________________

Step Totals	325.00	353.87	0.92	467.95	913.70	13.64	3.94	0.0%/0.0%/0.0%

Cum. Totals	325.00	353.87	0.92

Step #2	Load Step #2

Fixed Fire Pump  (20.000 kW, 3 phase, code F, unloaded, fire pump motor, w/ wye-delta starting)

1	20.00	23.45	0.85	24.74	88.53

Sprinkler Pump  (40.000 kW, 3 phase, code F, unloaded, fire pump motor, w/ wye-delta starting)

1	40.00	48.20	0.83	43.50	180.86

Jockey Pump  (5.000 kW, 3 phase, code H, unloaded, fire pump motor, w/ A.T.L. starting)

1	5.00	5.75	0.87	13.60	35.47

____________________________________________________________________

Step Totals	65.00	77.38	0.84	81.84	304.52	7.90	0.12	0.0%/0.0%/0.0%

Cum. Totals	390.00	431.26	0.90

____________________________________________________________________

Grand Totals	390.00	431.26	0.90					0.0%/0.0%/0.0%

___________________________________________________________

Informational

Program Version	8.0.0

Database Version	1.6

Project Created	December 22, 2020; 07:22:14 PM

Project Last Saved	December 22, 2020; 07:22:14 PM

Report Created	December 22, 2020; 08:12:58 PM

Project Created By